## Sheet1
Equation 1 | Calculating Chlorine Feed Rate
| Flow (MGD) | Desired Chlorine Dosage (mg/L) | Chlorine Strength (%)* | Chlorine Feed (lbs/day)
| 2 | 10 | 100% | 166.8
Input your average flow rate in millions of gallons per day (MGD), desired chlorine dosage (mg/L), and chlorine solution strength (%) to calculate the required chlorine feed rate (lbs/day) needed to achieve this dosage, which is highlighted in purple. *Chlorine strength will be 100% for gas, 12-15% for liquid hypochlorite, and 65-75% for granular/ tablet chlorine.
Equation 2 | Calculating Required Chlorine Dosage
| Flow (MGD) | Desired Chlorine Residual (mg/L) | Chlorine Strength (%)* | Typical Chlorine Demand (mg/L) | Required Chlorine Dosage (mg/L) | Required Chlorine Feed (lbs/day)
| 2 | 0.1 | 100% | 8 | 8.1 | 135.108
Input your average flow rate (MGD), desired chlorine residual (mg/L), chlorine solution strength (%), and typical chlorine demand (mg/L), to calculate your required chlorine dosage (mg/L) and required chlorine feed rate (lbs/day), which are highlighted in purple. The chlorine residual should be determined by your NPDES permit or other regulatory requirements. The typical chlorine demand is determined by troubleshooting and usually ranges between 5-20 mg/L for wastewater after biological treatment. *Chlorine strength will be 100% for gas, 12-15% for liquid hypochlorite, and 65-75% for granular/ tablet chlorine.
Equation 3 | Chlorine Residual
| Flow (MGD) | Chlorine Feed (lbs/day) | Chlorine Strength (%)* | Chlorine Demand (mg/L) | Chlorine Dosage (mg/L) | Chlorine Residual (mg/L)
| 2 | 125 | 100% | 7 | 7.494 | 0.494
Input your average flow rate (MGD), chlorine feed rate (lbs/day), chlorine solution strength (%), and typical chlorine demand (mg/L), to calculate your corresponding chlorine dosage (mg/L) and required chlorine residual (lbs/day), which is highlighted in purple. The typical chlorine demand is determined by troubleshooting and usually ranges between 5-20 mg/L for wastewater after biological treatment. *Chlorine strength will be 100% for gas, 12-15% for liquid hypochlorite, and 65-75% for granular/ tablet chlorine.